SECTION 166_ _ 
SURGE PROTECTIVE DEVICES (SPD)
FORMALLY KNOWN AS TRANSIENT VOLTAGE SURGE SUPPRESSION (TVSS)
PART 1 GENERAL

1.01 
DESCRIPTION:


A.
This section describes the materials and installation requirements for Surge Protective Devices, (SPD), formally known as Transient Voltage Surge Suppressors (TVSS), as shown on the drawings and herein specified at main and branch circuit distribution panels.

1.02
RELATED SECTIONS:

A. General Electrical Requirements.

B. Basic Electrical Materials and Methods.

C. Building Wire and Cable.

D. Switchboards.

E. Panelboards.

1.03
REFERENCES:

A. ANSI/IEEE C62.41-1991 and C62.45-1992.

B. National Electrical Manufacturers Association (NEMA LS1).

C. National Fire Protection Association (NFPA 70).

D. Underwriters' Laboratories (UL 1449 Edition 3.0).

1.04
SUBMITTALS:

A. Submit shop drawings for equipment and component devices under provisions of Section(s) [_______].
B. For each SPD indicated:

1. Product Data Sheets in NEMA LS-1 format - Publication for Low Voltage Surge Protection Devices (SPDs).

2. Installation and Operating Instructions.

3. UL 1449 Edition 3.0 Listing Certificate verifying the following:

a. Voltage Protection Rating, VPR

b. Nominal Discharge Current, In
c. SPD Type Listing

d. Maximum Continuous Operating Voltage, MCOV

e. Short Circuit Current Rating, SCCR

4. Voltage Protection Levels, Let-through voltage test results to UL 1449 Edition 3.0, Nominal Discharge Current test levels at 20 kA. 

5. Independent test report showing product meets manufactures claimed single shot surge rating.

1.05
MANUFACTURER’S QUALIFICATIONS:

A. Manufacturers shall be ISO9000 certified.

B. Manufacturers shall have been engaged in the design and manufacturing of surge protection devices for at least ten (10) years.

C. The following manufacturers will be approved, provided they meet all specifications:

1. Omega Power Systems, Inc,  Stuart, Florida

2. Other manufacturers approved by engineering in writing 10 days prior to bid date of project.

1.06
WARRANTY:

A. The manufacturer shall provide a minimum of five (5) year warranty on all panel type SPD products from the date of shipment against failure when installed in compliance with national and local electrical codes; and per the manufacturer’s installation, operation and maintenance manuals.   
PART 2 PRODUCTS:

2.01

GENERAL REQUIREMENTS:

A. The Surge Protection Device shall be listed to UL 1449 Edition 3.0 as a Type 1 SPD.

B. The UL 1449 Edition 3.0 Nominal Discharge Current (In) for the Surge Protection Device shall be 20 kA.  A Surge Protection Device with a UL 1449 Edition 3.0 Nominal Discharge Current  of 3 kA, 5 kA or 10 kA will not be accepted.

C. The Surge Protection Device shall have a stand-off voltage rating twice the nominal voltage. The Surge Protection Device shall be able to withstand Temporary Over Voltage Conditions twice the nominal voltage for an indefinite period of time, without damage, removing components from the circuit, or interrupting power.

D. The Surge Protection Device shall protect all modes via L-N, L-G and N-G modes of protection. For Delta power systems L-L and L-G protection modes shall be provided, with the ability to configure L-G to L-L for ungrounded systems.

E. Independent certification shall be provided proving that the Surge Protection Device meets the required 8/20µs per phase single shot surge rating, without failure of any fusing, disconnects or surge module. Bypassing of any fusing/disconnects for purpose of this test is not acceptable.

F. Each mode of the Surge Protection Device shall be rated to exceed the life cycle testing of ANSI/IEEE C62.45 by withstand of at least 200 operations at 10kA 8/20µs and at least 100 operations at 20 kA without failure. 

G. The Surge Protection Device shall have a Short Circuit Current Rating (SCCR) of 200 kAIC, per UL 1449 Edition 3.0.

H. The Surge Protection Device shall be capable of withstanding multiple temporary over-voltages per UL 1449 Edition 3 Section 36 “Overvoltage Test”, & 37 “Abnormal Overvoltage Tests” without failure or need to reset or replace modules/fuses.

I. Each MOV shall be protected with thermal disconnect devices and automatic disconnection of any MOV exhibiting excessive temperature. The following are not acceptable:

1.
Surge Protection Devices without thermal fuses/disconnects.

J. Enclosure shall:

1. Feature all metal NEMA 4 enclosure suitable for outdoor usage.

2. The Surge Protection Device depth shall be less than 3.5” to allow mounting within wall cavity with optional flush mount kit.

3. The Surge Protection Device width shall be less than 5” to enable installation between adjacent electrical enclosures.

2.02
High Energy Exposure: Main Service Switchgear (IEEE Category C Locations):
Surge Protection Devices shall be installed at all AC service entrances of each building and/or high exposure locations and/or as shown on the drawings:
A. The SPD shall by TYPE 1 UL1449 Edition 3.0.  (Type 2 is not acceptable)
B. The Surge Protection Device shall incorporate 200kA 8/20µs MOV protection per phase with a 50kA minimum peak rating per individual MOV.
C. The SPD shall have one LED status indication light per phase.
D. The SPD shall have Nominal Discharge Current (In) of 20 kA.  (10kA or less is not acceptable)
E. The SPD shall have an SCCR rating of 200kAIC without the use of an external circuit interrupt.
F. To avoid unsafe ground leakage current, filtering (capacitance) shall not connect to ground.  This specifically excludes or disallows any product claiming Sine Wave tracking, Active tracking, or any other capacitive based filtering protection that connects to the ground mode.
G. OMEGA POWER, model: FDC_ _ _ _  Compact or Modular Series or approved alternate.

2.03
Medium Energy Exposure: Switchgear Locations (IEEE Category B and C locations):
Surge Protection Devices shall be installed at all Distribution switchgear and small AC service entrances of each building and/or high exposure locations and/or as shown on the drawings.
A. The SPD shall by TYPE 1 UL1449 Edition 3.0.  (Type 2 is not acceptable).  

B. The Surge Protection Device shall incorporate 100kA 8/20µs MOV protection per phase with a 50kA minimum peak rating per individual MOV.  

C. The SPD shall have one LED status indication light per phase.  

D. The SPD shall have Nominal Discharge Current (In) of 20 kA.  (10kA or less is not acceptable).  

E. The SPD shall have an SCCR rating of 200kAIC without the use of an external circuit interrupt.  

F. To avoid unsafe ground leakage current, filtering (capacitance) shall not connect to ground.  This specifically excludes or disallows any product claiming Sine Wave tracking, Active tracking, or any other capacitive based filtering protection that connects to the ground mode.  

G. OMEGA POWER, model: FDB_ _ _ _  Compact or Modular Series or approved alternate.

2.04
Medium to Low Energy Exposure: Branch Panel Locations (IEEE Category A and B locations):

Surge Protection Devices shall be installed at all Branch Panel switchgear and at specific point of use equipment disconnect locations and/or as shown on the drawings.
A. The SPD shall by TYPE 1 UL1449 Edition 3.0.  (Type 2 is not acceptable).  

B. The Surge Protection Device shall incorporate 50kA 8/20µs MOV protection per phase with a 50kA minimum peak rating per individual MOV.  

C. The SPD shall have one LED status indication light per phase.  

D. The SPD shall have Nominal Discharge Current (In) of 20 kA.  (10kA is not acceptable).  

E. The SPD shall have an SCCR rating of 200kAIC without the use of an external circuit interrupt.  

F. To avoid unsafe ground leakage current, filtering (capacitance) shall not connect to ground.  This specifically excludes or disallows any product claiming Sine Wave tracking, Active tracking, or any other capacitive based filtering protection that connects to the ground mode.  

G. OMEGA POWER, model: FDA_ _ _ _  Compact Series or approved alternate.

PART 3 EXECUTION:

3.01

INSTALLATION:

A. At locations indicated on drawing(s), install Surge Protection Devices in full accordance with manufacturer’s written instructions and comply with all applicable NEC codes.

B. Use safe practices when installing any SPD.  DO NOT install ‘hot’ or on energized switchgear locations.  Use OSHA approved safety gear and safe practices for all installations.  Must be installed by a licensed electrician.  Failure to follow safe practices or installations performed by personnel not licensed as electricians will void manufacturers warranty.

C. All SPD products approved by this specification are TYPE 1 Listed.  While this allows for installation without additional circuit interrupt, we highly recommend the use of an independent (and internal to the switchgear) Circuit Breaker that will serve as a means of disconnect for servicing the Surge Protection Device thus allowing the protected panel to remain energized during servicing.  Manual Disconnect switches that are external to the switchgear panel that add additional wire lead length to the installation are not allowed.
D. SPD shall be installed per manufacturer’s installation instructions with wire lead lengths as short and as straight as possible without sharp bends in the wire and not to exceed the wire length provided with the SPD (24”).  6” to 12” wire lead length is optimum, whenever possible.  Splicing additional wire length to the leads provided with the SPD is not allowed.
E. Before energizing, the installer shall verify service ground is properly bonded to the installation location.  Unbonded or separately derived grounds including but not limited to additional and isolated ground rods, building steel, or pressurized water pipe derived grounds are not allowed.  Failure to properly test and bond the SPD to the service ground will void the manufactures warranty.

END OF SECTION

 

Revised February 6, 2012
Page 1 of 4
 

